## Boiler
BOILER AND STEAM GENERATOR EMISSION CALCULATIONS (Ver. 7.0)
Attachment:
Permit Number:
Facility:
Heater Input Data
| Information |  | Value | Units | Reference
| Maximum Hourly Heat Input…………… |  | 2 | MMBtu/hr | Permit Application
| Daily Operating Schedule...................... |  | 24 | hrs/day | Permit Application
| Maximum Daily Heat Input……………. |  | 48 | MMBtu/day | Calculated value
| Yearly Load Factor (%)......................................... |  | 100 | % | Permit Application
| Maximum Annual Heat Input………….. |  | 17520 | MMBtu/yr | Calculated value
Fuel Information
| Information |  | Value | Units | Reference
| Fuel........................................................... |  | PUC N.G. | N/A | Permit Application
| High Heating Value......................................... |  | 1050 | Btu/scf | Permit Application
| Sulfur Content of Fuel.................................... |  | 80 | ppmvd as H2S | Permit Application
Emission Factors
| Pollutant |  | Value | Units | Reference
| NOx Emission Factor...................................... |  | 0.0244 | lb/MMBtu | District Rule 360 (20 ppmvd @ 3% O2)
| ROC Emission Factor................................. |  | 0.0054 | lb/MMBtu | AP-42, Section 1.4
| CO Emission Factor............................................ |  | 0.297 | lb/MMBtu | District Rule 360 (400 ppmvd @ 3% O2)
| SOx Emission Factor..................................... |  | 0.013681 | lb/MMBtu | Mass Balance Calculation
| PM Emission Factor ........................................... |  | 0.0075 | lb/MMBtu | AP-42, Section 1.4
| PM10 Emission Factor.......................................... |  | 0.0075 | lb/MMBtu | AP-42, Section 1.4
| PM2.5 Emission Factor........................................... |  | 0.0075 | lb/MMBtu | AP-42, Section 1.4
Boiler/Steam Generator Potential to Emit
| Pollutant | lb/day | TPY
| NOx | 1.1712 | 0.21374
| ROC | 0.2592 | 0.047304
| CO | 14.256 | 2.6017
| SOx | 0.65669 | 0.11985
| PM | 0.36 | 0.0657
| PM10 | 0.36 | 0.0657
| PM2.5 | 0.36 | 0.0657
| Processed By: |  |  |  | Date: