Applicability Flowchart for NESHAP for Reciprocating Internal Combustion Engines (RICE)

40 CFR 63, Part ZZZZ

Do you own or operate a Stationary RICE?

Your facility is not subject to this subpart.

Is the RICE being operated to test it at a test cell/stand or is it part of a test cell/stand?

The RICE will be covered under 40 CFR Part 63, Subpart PPPPP.

START

YES

NO

YES

NO

Note: Any unit beyond this point is an affected unit of this subpart and should be, at a minimum, identified as such in any relevant permits.

Is the RICE a compression ignition RICE or a spark ignition RICE?

Go to page 2.

Go to page 3.

COMPRESSION

IGNITION

SPARK

IGNITION

This flowchart was developed by Mississippi Department of Environmental Quality, Air Division, 3/2011.

Applicability Flowchart for Compression Ignition RICE1

Is the facility a major source or area source of HAP?

Is the CI RICE new2 or existing?

(June 12, 2006)

Is the CI RICE

> 500 BHP?

Is the CI RICE new2 or existing?

(December 19, 2002)

YES

NO

EXISTING

NEW

Is the CI RICE new2 or existing?

(June 12, 2006)

NEW

NEW

EXISTING

EXISTING

Does the CI RICE burn digester gas or landfill gas equivalent to > 10% of the gross heat input annually?

YES

NO

Meet the initial notification requirements (§63.6645(f))

Monitor and record fuel usage daily (§§63.6625(c) & 63.6655(c))

Submit an annual report (§63.6650(g))

The RICE is NOT subject to emission and operating limits of this subpart.

Meet the emission limits in Table 2a & the operating limits in Table 2b.

Is the CI RICE an emergency RICE or a limited use RICE?

YES

The CI RICE must meet the initial notification requirements in §63.6645(f).  If the CI RICE is an emergency RICE, the unit must also comply with the requirements in §63.6640(f); otherwise, there are no other requirements in this subpart or Subpart A, General Provisions.

NO

Is the CI RICE

an emergency RICE, a limited use RICE, or burn digester gas or landfill gas equivalent to > 10% of the gross heat input annually?

YES

The CI RICE does not have to meet the requirements of this subpart or Subpart A, General Provisions.

Meet the emission limits in Table 2c & the operating limits in Table 2b.3

NO

Am I subject to NSPS Subpart IIII?

NO

Comply with NSPS.

YES

MAJOR

AREA

Am I subject to NSPS Subpart IIII?

The CI RICE does not have to meet the requirements of this subpart or Subpart A, General Provisions.

Comply with NSPS.

YES

NO

Is the CI RICE

a residential, commercial, or institutional emergency RICE?

Meet the emission limits in Table 2d & the operating limits in Tables 1b and 2b.3

YES

NO

Meet the emission limits in Table 2c.3

The CI RICE does not have to meet the requirements of this subpart or Subpart A, General Provisions, except emergency RICE must comply with the requirements in §63.6640(f).

The CI RICE does not have to meet the requirements of this subpart or Subpart A, General Provisions, except for the requirements in §63.6640(f).

1 Additional monitoring, installation, collection, operation, and maintenance requirements in §63.6625 may apply.

2 For the purpose of this flowchart, new also includes reconstructed.

3 If your CI RICE is a non-emergency, non-black start unit with a site rating of more than 300 BHP and a displacement of less than 30 L/cylinder that uses diesel fuel, you must use diesel fuel that meets the requirements in 40 CFR 80.510(b) for nonroad diesel fuel.

Page 2							This flowchart was developed by Mississippi Department of Environmental Quality, Air Division, 3/2011.

Applicability Flowchart for Spark Ignition RICE1

Is the facility a major source or area source of HAP?

Is the SI RICE new2 or existing?

(June 12, 2006)

Is the SI RICE

> 500 BHP?

Is the SI RICE new2 or existing?

(December 19, 2002)

YES

NO

EXISTING

NEW

Is the SI RICE new2 or existing?

(June 12, 2006)

NEW

EXISTING

EXISTING

Does the SI RICE burn digester gas or landfill gas equivalent to > 10% of the gross heat input annually?

YES

NO

Meet the initial notification requirements (§63.6645(f))

Monitor and record fuel usage daily (§§63.6625(c) & 63.6655(c))

Submit an annual report (§63.6650(g))

The RICE is NOT subject to emission and operating limits of this subpart.

Meet the emission limits in Table 2a & the operating limits in Table 2b.

Is the SI RICE an emergency RICE or a limited use RICE?

YES

The SI RICE must meet the initial notification requirements in §63.6645(f). If the SI RICE is an emergency RICE, the unit must also comply with the requirements in §63.6640(f); otherwise, there are no other requirements in this subpart or Subpart A, General Provisions.

NO

Is the SI RICE

an emergency RICE, a limited use RICE, a 2 or 4 stroke lean burn RICE, or burn digester gas or landfill gas equivalent to > 10% of the gross heat input annually?

Am I subject to NSPS Subpart JJJJ?

Is the SI RICE a 4 stroke rich burn RICE?

NO

Is the SI RICE a 4 stroke lean burn ≥ 250 BHP manufactured on or after January 1, 2008?

NO

Meet the emission limits in Table 2a & the operating limits in Table 2b.

YES

Meet the emission limits in Table 2c.

MAJOR

AREA

Am I subject to NSPS Subpart JJJJ?

The SI RICE does not have to meet the requirements of this subpart or Subpart A, General Provisions.

Comply with NSPS.

YES

NO

Is the SI RICE

a residential, commercial, or institutional emergency RICE?

Comply with NSPS.

YES

The SI RICE does not have to meet the requirements of this subpart or Subpart A, General Provisions.

NO

YES

NO

Meet the emission limits in Table 1a & the operating limits in Table 1b.

Is the SI RICE a 2 or 4 stroke lean burn RICE?

YES

NO

Is the SI RICE a 4 stroke rich burn RICE?

Meet the emission limits in Table 1a & the operating limits in Table 1b.

YES

NO

The SI RICE does not have to meet the requirements of this subpart or Subpart A, General Provisions.

Is the SI RICE

a limited use RICE or burn digester or landfill gas equivalent to > 10% of the gross heat input annually?

YES

NO

Meet the emission limits in Table 2d & the operating limits in Tables 1b and 2b.

The SI RICE does not have to meet the requirements of this subpart or Subpart A, General Provisions, except emergency RICE must comply with the requirements in §63.6640(f).

YES

NEW

NO

YES

The SI RICE does not have to meet the requirements of this subpart or Subpart A, General Provisions, except for the requirements in §63.6640(f).

Is the SI RICE an emergency RICE?

NO

YES

1 Additional monitoring, installation, collection, operation, and maintenance requirements in §63.6625 may apply.

2 For the purpose of this flowchart, new also includes reconstructed.

3 If your CI RICE is a non-emergency, non-black start unit with a site rating of more than 300 BHP and a displacement of less than 30 L/cylinder that uses diesel fuel, you must use diesel fuel that meets the requirements in 40 CFR 80.510(b) for nonroad diesel fuel.

Page 3							This flowchart was developed by Mississippi Department of Environmental Quality, Air Division, 3/2011.